Auditing form to assess EN 14181 reports

Published October 2020

The forms below can be used to assess EN 14181 test reports.

Environment Agency TGN M20 – quality assurance of continuous emissions monitoring systems, specifies the format for reporting the results of the functional tests specified in EN 14181. It also specifies the contents and their order for test reports for QAL2 and ASTs.

Form A is for the main body of the report and Form B for the functional tests.

Non-compliances are noted in the right-hand column and labelled sequentially, together with a description of the non-compliance. A more detailed description is included in a summary of the findings, recorded on Form C. Non-compliances are classified as major or minor. The following are major non-compliances:

- Missing data in the report, e.g. where there is evidence of a selective use of data, or an insufficient number of samples (unless justified in the report).
- Incorrect calculations.
- Several related non-compliances which show a pattern, e.g. several missing parts of the report.
- Evidence of a lack of understanding of the workings of the CEMS and peripheral determinands.

All other non-compliances are classified as minor. An observation is an example of where the test laboratory can improve its reporting procedures.

Form A - BS EN 14181 QAL2/AST Report Check Form
Consultant
Operator
Installation name
Permit number
Date of Report
Report version number
Job reference number
Details/items to be checked			Checked	Comments
Section 1 Executive Summary and title pages
Section 1A
Operator name, address and primary contact
Type of process
Installation name
Permit number
Dates of the tests
Date and version number of the report
Test laboratory name, address, tel number, email address and UKAS ref number
Report author
Report approver
Section 1B
AST or QAL 2
Stack designation
Determinands
Value for ‘a’ in calibration function
Value for ‘b’ in calibration function
Valid calibration range based on calibrated CEMs data from the QAL 2
Valid calibration range based on calibrated CEMs data from the AST
Extrapolated range based on reference materials
Pass or fail statement for the variability test
Pass or fail statement for the acceptance test (AST)
Statement to confirm calibration function remains valid when no adjustments are made to CEMs
Section 1C
Deviations from SRMs and reasons
Deviations from BS EN 14181 and reasons
Impacts on results
Actions required
Section 2 Information on installation and provisions for monitoring
2.1 Regulatory information
2.1.1 Operator name
2.1.2 Installation name
2.1.3 Installation address
2.1.4 Sector for the installation
2.1.5 Permit number
2.1.6 Date of the last QAL2 / AST
2.1.7 Determinands and emission limit values
2.2 Operational Information & monitoring provisions
2.2.1 Process type and variations
Continuous or batch
Expected emissions and variations
Other factors affecting the results
Review of historical data
Provisions to deal with low readings
Checks on CEMs reading zero
2.2.2 Type of fuel
Fuel used during the tests
Types & proportions of fuels for co-incineration
2.2.3 Abatement
Type of abatement & affects on emissions
2.3 Monitoring provisions for periodic monitoring
2.3.1 Stack and sampling ports
Rectangular or round stack
Dimensions/diameter of stack
Location of sampling ports
Number of sampling ports
Diagram / photos of emission points, platform
2.3.2 Platform and site provisions
Safe, with adequate space & weather protection
Safe access to CEMs
Adequate supplies of reference materials, tools, & spares
Facilities to introduce reference materials
Degree of compliance with MID 15259
2.3.2 Provision for representative samples
Grid measurements compliant with MID 15259
Ratio of highest to lowest flow rates
2.4 Continuous emission monitoring systems
2.4.1 Types of CEMs
Type e.g. cross duct, in-situ or extractive
Brand
Model
Certification range
Principle
Location of sampling / measurement
Statement of QAL 1 compliance
Is moisture measured or calculated
2.4.2 Types of monitoring for peripheral determinands
Temperature & pressure. Are they recorded

Section 3 Information about the monitoring campaign
3.1 Details of test laboratory staff
Name, MCERTS reg number, level, expiry date
3.2 Standard reference methods
Determinand
SRM standard applied
Type and principle
Operational range
Certification range of instrumental methods
Uncertainty
UKAS accreditation
Section 4A Monitoring data and calculations Section 4A for QAL 2, section 4B for AST
A4.1 Table 4.1 Raw monitoring data
Start & end times of each pair of data
Raw CEMs results
Stack/CEM peripheral determinands. Temperature, pressure, oxygen, moisture
Raw SRM results
SRM peripheral determinands. Temperature, pressure, oxygen, moisture
SRM results expressed under the same conditions as the CEMs results
A4.2 Table 4.2 Standardised monitoring data
Standardised CEM results (STP)
Standardised SRM results (STP)
A4.3 Plot 1
Time series of standardised CEM v SRM data
A4.4 Elimination of outliers
A4.5 Determination of procedure A or B
A4.6 Data used to determine calibration function
SRM & CEMs results expressed the same
Raw CEM results
A4.7 Determination of calibration function
A4.8 Calculation of calibrated CEM values
Raw CEMs values
Calibrated CEM values at stack conditions
Peripheral determinands for CEMs
Calibrated CEMs values standardised
A4.9 Plot 2
x – y plot of CEMs v SRM data at conditions measured by CEM
Calibration function, including R2 value for method A
A4.10 Data used for variability/acceptance tests
Calibrated CEMs values standardised
SRM values standardised
Difference between each pair of values
Difference minus average of differences
Difference minus average of differences squared
A4.11 Calculations of variability/acceptance tests
Calculations set out as per BS EN 14181
The variability test
Statement of results
A4.12 Plot 3
x – y plot of calibrated standardised CEM data v standardised SRM data
Indication of the valid calibration range
Extrapolation of the valid calibration range using surrogates
Parallel lines included. 95% CI of daily average ELV
Section 4B Monitoring data and calculations - AST
B4.1 Raw monitoring data
Start & end times of each pair of data
Raw CEMs results
Stack/CEM peripheral determinands. Temperature, pressure, oxygen, moisture
Raw SRM results
SRM peripheral determinands. Temperature, pressure, oxygen, moisture
SRM results expressed under the same conditions as the CEMs results
B4.2 Table 4.2 Standardised monitoring data
Standardised CEM results
Standardised SRM results
B4.3 Plot 1
Time series of standardised CEM v SRM data
B4.4 Elimination of outliers
B4.5 Data used to calculate calibrated values
Raw CEM values
Original calibration function from previous QAL2
Calibrated CEM values at stack conditions
Peripheral determinands for CEMs
Calibrated CEM values, standardised
Standardised SRM values
B4.6 Data used for variability test
Calibrated CEMs values standardised
SRM values standardised
Difference between each pair of values
Difference minus average of differences
Difference minus average of differences squared
B4.7 Variability test and acceptance test
Calculations set out as per BS EN 14181
The variability test
The acceptance test
Statement of results
B4.8 Plot 2
x – y plot of calibrated standardised CEM data v standardised SRM data
Indication of the valid calibration range
Parallel lines included. 95% CI of daily average ELV
Extrapolation of valid calibration range, using surrogates, if applied
Section 5 Results of the functional tests
5.1 Results of functional tests
5.2 Information on test personnel
Name of person/s performing the functional tests
Name of person witnessing the tests where applicable
Notes:
Checked by					Date

Form B - EN 14181 Functional-Tests Report Check-Form
Consultant
Operator
Installation name
Permit number
Date of Report
Report version number
Job reference number

Details/items to be checked			Checked	Comments
1. Alignment and cleanliness (Non extractive CEMs)
Internal check of the CEM
Cleanliness of the optical components
Flushing air supply
Obstructions in the optical path
Alignment of the measuring system
Internal check of optical surfaces for contamination
2. Sampling Systems
Sampling probe
Gas conditioning systems
Pumps
All connections
Sample lines
Power supplies
Filters
NOx converter (If applicable) – Date and results of last efficiency test
General condition of sampling system
3. Leak testing
Leak test of entire sampling system
4. Zero and span check
Reference zero and span materials shall be used to verify the corresponding readings of the CEM
Non extractive CEMs – zero and span checks to be performed using a reference path free of flue gas
5. Linearity (AST only)
During the calibration/linearity tests the applied concentrations should be logged onto the DCS to prove the complete system i.e. concentration applied to the instrument is represented by the instrument output and identical to the value logged on the DCS. DCS values should be included in the instrument service report.
Linearity of the CEM’s response shall be checked using 5 different reference materials including a zero concentration
The reference material with zero concentrations, as well as the reference materials with 4 different concentrations, shall have a verifiable quantity and quality
For gaseous reference materials, the 4 reference materials can be obtained from different gas cylinders or can be prepared by means of a dilution system from a single gas concentration
Reference materials concentrations shall be approximately 20%, 40% , 60% and 80% of the range of the short term emission limit. The dry test reference material shall be applied to the inlet of the CEM
CEMs are tested using the following concentrations in a randomised sequence
Reference material with zero concentration
Reference material concentration approximately 20% of the short term ELV
Reference material concentration approximately 40% of the short term ELV
Reference material concentration approximately 60% of the short term ELV
Reference material concentration approximately 80% of the short term ELV
Reference material with zero concentration
After each change in concentration, the first instrument reading shall ordinarily be taken after a time period equal to at least 3 times the response time of the CEM. At each reference material concentration at least 3 readings shall be made, 6 readings shall be taken at zero. The time period between the start of each of the 3 readings shall be separated by at least 4 times the response time. / The test lab may apply a risk-based approach to linearity testing in order to reduce the time for the tests. For example, the readings may be taken after less than 3x the response time; however, if the CEM fails the linearity test, then the test lab shall repeat the linearity test and wait at least 3x the response time as stated above. Alternatively, the number of repetitions of the test may be reduced if the CEM passes the required performance criteria by a factor of at least 2 (i.e. half the allowable residual). Increasing the waiting time to 5x the response time, for example, may be a means of meeting this requirement. / Where no other method is possible, the linearity can also be performed with the aid of reference materials such as grating filters or gas filters. / The linearity shall be calculated and tested using the procedure as given in EN 14181 annex B. If the CEM does not pass this test, then the problem shall be identified and rectified.
6. Interferences (AST only)
A test shall be undertaken if the process gases to be monitored contain components that are known interferences, as identified during QAL 1 and there is a failure of the QAL2 or AST which could be due to interferences
7. Zero and span drift (Audit) (AST only)
The test lab shall assess whether the operator has a QAL3 procedure in place, and whether the operator has applied this procedure. The evidence would comprise (i) a documented procedure(ii) zero and span data(iii) control chart
8. Response time
The response time of the CEM shall be checked. This can be performed, if appropriate, by feeding of the reference material at the end of the sampling probe. The response time shall not exceed the performance requirement applied during the QAL1 tests.
9. Service report
Document reference for work instruction for the type of work being undertaken
Instrument manufacturer
Instrument type
Instrument model
Instrument serial number
Operating principle
Operating range
Certification details
Compliance with MCERTS including certificate number
Location
Date and time when the work was undertaken
Equipment used – type, serial numbers, calibration dates
Gases used – certificate numbers, expiry dates, binary / mix
NOx-converter efficiency-test, if applicable
Calibration and linearity data as required by EN 14181
Logged data for period of calibration and linearity. Lab shall provide an explanation if there are gaps in the data
Name and signature of service engineer
Checked by					Date

Form C – Report Summary
AUDIT REPORT		NO.:
Select (x) the Audit type below: / Data Verification X / or / On Site / Audit of:
Purpose of Audit: / To verify the QAL 2/AST report, [add report reference as applicable] Specifically: / To ensure the supporting data used to perform the QAL 2/AST procedure is fit for purpose. / To ensure the derived calibration functions are correct. / To verify the CEM meets the required uncertainty allowances.
Scope of Audit: / A check of emission reporting criteria against those stated in the permit / Review of MCERTS QAL 2/AST report / Review of results from the functional tests
Auditors/Verifiers:	Auditee:

Report completed by: / Date:			Distribution:

1. Summary / The audit assessed the report for compliance with the requirements of EN 14181, and the Technical Guidance Note M20. The findings from the exercise comprise [add as applicable] / 2. Required actions / 3. Non-compliances / 3.1 Major non-compliances / 3.2 Minor non-compliances / 4. Observations / 5. Review of results from the functional tests

GEHO0811BUFE-E-E